Vicon® Industries V2360W OUTDOOR IP PANORAMIC DOME CAMERA 
	SECURITY SYSTEM
28 23 00 VIDEO SURVEILLANCE

PART 2 - PRODUCTS

2.01	GENERAL

A.	All equipment and materials used shall be standard components that are regularly manufactured and used in the manufacturer’s system.

B.	All systems and components shall have been thoroughly tested and proven in actual use.

C.	All systems and components shall be provided with the availability of a toll free 24- hour technical support phone number from the manufacturer. This no charge service shall be available to dealers and installers.

2.02	OUTDOOR IP PANORAMIC DOME CAMERA 

A.	The outdoor panoramic dome camera shall incorporate a fixed camera/lens combination. The camera dome shall be available for indoor/outdoor surface mounting. The high-resolution day/night camera be available in a 12 MP resolution model and shall have WDR and Smart IR capability and shall include an integral fixed fisheye lens. This lens shall provide an extremely wide angle of view for a panoramic image, capturing a 180°panoramic view and a 360° surround view at full HD resolution. Day/night operation shall be achieved using a built-in IR-cut filter. IR distance shall be 49 ft (15 m) with 1 IR LEDs. 

B.	The camera shall provide a high-resolution hemispherical view and shall provide crisp distortion free images and support web de-warping.

C.	A variety of mounting options shall be available. 

D.	The panoramic dome camera shall be powered by PoE+ or 24 VAC. A dual heater system shall be provided that maintains proper temperature in the camera housing and prevents fogging of the window.

E.	The panoramic dome camera shall have triple streaming video and support H.264/H.265 and M-JPEG compression. The camera shall also have smart encoding to further improve video encoding and improve storage capacity

F.	Camera features shall include electronic iris, AGC, WDR, white balance, defog, flip, privacy masking, dynamic ROI and motion detection. It shall have Video Content Analysis (VCA) of tampering/defocus and motion.

G.	The panoramic dome camera shall meet the FCC requirements for a Class A device. It shall include support for the industry-standard ONVIF S/T/G/Q interface. It shall be IP67-rated to withstand rain, dust and vandalism and IK10 rated for impact resistance. The camera shall meet the latest regulations required to be NDAA, GSA schedule and TAA approved.

H.	The panoramic dome camera shall provide a slot for an SD card for local storage.

I.	The panoramic dome camera shall meet or exceed the following design and performance specifications.

2.03	DAY/NIGHT IP PANORAMIC DOME CAMERA SPECIFICATIONS

A.	Imaging Device:	1/1.7-inch 
B.	Max. Resolution:	12 MP 
C.	Shutter Speed:	1/2 - 1/10,000 sec
D.	Automatic Gain Control:	On/Off selectable
E.	Sensitivity (@30 IRE):	Color: 0.04 lux; B&W: 0.03 (IR Off), 0 lux (IR On)
F.	Digital Zoom:	Dynamic ROI
G.	Lens Adjustment:	Fixed Fisheye
H.	Focal Length:	1.2 mm 
I.	Field of View:	195° (at full resolution); 360° surround view
J.	IR Distance:	Smart IR; 49 ft (15 m) with 1 IR LED
K.	Dual Heater System:	For low temperature operation: heater turns on at -40° F 
                                             (-40° C) and off at 59° F (15° C). 
                                             For defog operation: heater turns on at -40° F and off at
                                             140° F (60° C).

2.04	ELECTRICAL SPECIFICATIONS

A.	Input Voltage:	PoE+ or 24 VAC
B.	Current:	PoE: 0.52 A; 24 VAC: 1.1 A
C.	Power Consumption:	IR On: 25 W; IR off: 12.2 W
D.	Connectors:	Optional backbox available for cabling
                                             PoE Power: RJ-45; 24 VAC: terminal block
		Video/Data: RJ-45
		Audio In/Out: screw terminal; built-in mic; audio level alarm alert
		Slot for SD card (128 G max customer supplied card)
		Reset button
		Default button
E.	Radio Frequency	
	Emission Rating: 	FCC Class A; CE

2.05	ENVIRONMENTAL SPECIFICATIONS

A.	Operating Temperature:	-40° to 122°F (-40° to 50°C)
	
B.	Humidity:	Up to 90% relative, non-condensing

2.06	PHYSICAL SPECIFICATIONS

A.	Construction:	Aluminum alloy housing; PC+ABS front case
B.	Dimensions:	Height: 2.2 in. (57 mm), 
Diameter: 5 in. (150 mm)
C.	Weight: 	2 lb (0.9 kg)

2.07	MECHANICAL SPECIFICATIONS

A.	Camera Mount:	Surface mount 

2.08	NETWORK VIDEO SPECIFICATIONS

A.	Communication Platform:	Open platform; compatible with Valerus 
	Video Management System 
B.	Compression:	Smart Encoding; H.264/H.265; M-JPEG 
C.	LAN Interface:	10 Base-T/100 Base-TX, Unicast/Multicast
D.	Video Channels	Triple streaming
E.	Resolution and Frame Rate:	4000x3000, 3000x3000, 2592x1944, 1944x1944, 048x1536, 1536x1536, 1280x960, 960x960, 800x600, 608x600, 640x480, 480x480, 230x240, 240x240
Max 30 fps 
F.	Web Browser:	Internet Explorer, Safari, Firefox, Chrome, Microsoft 
                                             Edge
G.	Users:	Live viewing for up to 10 clients
H.	Image Settings:	Digital image effects defog, flip; configurable 
                                             brightness, contrast, saturation, hue, sharpness; BLC; 
                                             HLC; gamma correction; 3 DNR; motion detection; 
	white balance, AGC; Electronic Shutter, automatic or 
	manual; digital zoom; motion detection; privacy masks;
                                             dynamic ROI
I.	Video Content Analysis 
(VCA):	Tampering/defocus, motion
J.	Supported Protocols:	IPv4/IPv6, TCP, HTTP, HTTPS, RTSP, RTCP, RTP, 
                                             RTMP, SMTP, SNMP v1/2c/3, UPnP, TLS/TTLS, FTP, 
                                             HLS, ICMP, IGMP, LDAP, NTP, DHCP, DNS, 
                                             DDNS, UDP, QoS, ARP, PPPoE, Bonjour, ONVIF 
                                             S/G/Q/T

2.09	CERTIFICATIONS

A.	CE
B.	UL
C.	FCC, Class A
D.	IP67
E.	IK10
F.	ONVIF S/T/G/Q
G.	RoHS
H.	NDAA/GSA/TAA compliant

2.10	WARRANTY

A.	5 years, parts and labor

2.11	APPROVED MANUFACTURERS

A.	The outdoor IP panoramic dome camera shall be Vicon Industries V2360W-12. 

END OF SECTION

Vicon is a registered trademark of Vicon Industries Inc. in the United States and other countries.